## 1. Own Sources
Example of Supporting Documentation for Volume from Own Sources
Treatment Plant Production (UNITS = AF)
| Month | Raw Water Influent | Backwash Estimation | Finished Water Meter
| 2016-01-01 | 848.89 | 16 | 830.859
| 2016-02-01 | 908.28 | 11 | 897.1354
| 2016-03-01 | 1058.18 | 14 | 1043.5378
| 2016-04-01 | 1125.35 | 32 | 1093.5562
| 2016-05-01 | 1255.24 | 11 | 1244.372
| 2016-06-01 | 1388.789 | 15 | 1373.1687
| 2016-07-01 | 1291.2573 | 11 | 1280.9129
| 2016-08-01 | 1189.45 | 14 | 1175.1438
| 2016-09-01 | 1165.5655 | 18 | 1147.2084
| 2016-10-01 | 955.8303 | 12 | 943.5001
| 2016-11-01 | 882.48 | 15 | 858.34
| 2016-12-01 | 961.4115 | 18 | 943.2225
| Audit Total | 13030.7236 | 187 | 12830.9567
NOTES
* Raw Water Influent meter measures flow into the treatment plant, 6" mag meter, SCADA readings provide 15-min average flows but no totalizer, used for plant operations
* Backwash meter measures diversion from finished water line back into the plant. This is located before the finished water meter
* Finished Water Meter captures treatment plant effluent conveyed into distribution. Totalizer manual reads taken daily alongside SCADA logging.
Reminders for Volume from Own Sources Supporting Documentation:
* volume produced per meter by month
* measuring raw or treated water?
* any backwash or flow to waste setups to account for?

## 2. VoS, WI, WE
Example of Supporting Documentation for all Water Supplied Volumes
Volume from Own Sources, Water Imported, Water Exported UNITS = MG
| Month | MWD TAP-01 | Well 1 | Well 2 | Well 3 | Neighbor Town | Monthly Distribution Totals | Water Audit Software Totals
| 2016-01-01 | 31.56 | 34.596 | 23.819 | 64.4899 | 0 | 154.4649 | Volume from Own Sources: | 1078.9373 | MG
| 2016-02-01 | 7.29 | 31.9424 | 22.195 | 61.8894 | 0 | 123.3168 | Water Imported: | 1309.24 | MG
| 2016-03-01 | 6.06 | 31.2232 | 21.7 | 61.1845 | 0 | 120.1677 | Water Exported: | 73.43 | MG
| 2016-04-01 | 58.44 | 35.5632 | 24.43 | 65.4377 | 0 | 183.8709
| 2016-05-01 | 125.48 | 15.3264 | 11.19 | 45.6057 | 0 | 197.6021
| 2016-06-01 | 170.61 | 0 | 55.48 | 30.5858 | 0 | 256.6758
| 2016-07-01 | 202.11 | 5.7536 | 60.5807 | 36.2243 | 0 | 304.6686
| 2016-08-01 | 185.45 | 2.0336 | 37.6729 | 32.5787 | 0 | 257.7352
| 2016-09-01 | 178.74 | 1.488 | 34.3131 | 32.044 | 0 | 246.5851
| 2016-10-01 | 171.39 | 0 | 25.15 | 0 | 5.18 | 191.36
| 2016-11-01 | 123 | 2.3064 | 39.3528 | 32.8461 | 45.79 | 151.7153
| 2016-12-01 | 49.11 | 5.4312 | 58.5953 | 35.9084 | 22.46 | 126.5849
| Audit Total | 1309.24 | 165.664 | 414.4788 | 498.7945 | 73.43 | 2314.7473
| Source | Notes
| MWD TAP-01 | All MWD imported water comes through MWD TAP-01, billed amounts shown here, hourly SCADA reads available for cross-reference, bi-annual calibration, no testing
| Well 1 | Each well pump has a 6" mag meter that's electronically calibrated once per year, all installed in 2013, daily manual reads and weekly compilation of well production data
Well 2
Well 3
| Neighbor Town | Flow provided to Neighbortown in the fall/winter when needed
Reminders for Water Supplied (VOS, WI, WE) Supporting Documentation:
* volume produced per meter by month
* measuring raw or treated water?
* any backwash or flow to waste setups to account for?
* any water-wheeling or special arrangments to account for?

## 3. AC
Example of Supporting Documentation for Billed Metered Authorized Consumption
Water Sold, UNITS = MG
| Month | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2016-04-01 | 2016-05-01 | 2016-06-01 | 2016-07-01 | 2016-08-01 | 2016-09-01 | 2016-10-01 | 2016-11-01 | 2016-12-01 | 2016 TOTAL
| Single Family Residential | 38.42 | 28.18 | 42.15 | 47.77 | 48.99 | 52.18 | 59.73 | 51.48 | 42.54 | 41.15 | 32.15 | 34.45 | 519.19
| Multi Family Residential | 18.536 | 17.836 | 18.487 | 17.654 | 19.285 | 21.336 | 24.367 | 19.894 | 19.684 | 16.898 | 15.526 | 15.015 | 224.518
| Commericial/Institutional | 8.778 | 8.9617 | 10.836 | 13.006 | 12.9121 | 11.7977 | 12.936 | 11.8141 | 12.278 | 10.836 | 12.9395 | 13.594 | 140.6891
| Industrial | 1.4 | 1.5 | 1.2 | 1.1 | 1.6 | 1.8 | 1.5 | 1.6 | 1.2 | 1.4 | 1.4 | 1.4 | 17.1
| Landscape Irrigation | 2.54 | 4.82 | 8.42 | 10.48 | 11.94 | 12.71 | 14.45 | 12.45 | 10.98 | 11.11 | 9.92 | 7.45 | 117.27
| Municipal | 2.2152 | 2.2462 | 2.5634 | 2.9305 | 2.9147 | 2.7261 | 2.9187 | 2.7289 | 2.8074 | 2.5634 | 2.9193 | 3.03 | 32.5637
| Water Department | 1.4952 | 1.5456 | 1.05 | 1.6632 | 1.2012 | 1.7136 | 1.554 | 1.4952 | 2.1336 | 1.218 | 1.3776 | 0.8232 | 17.2704
| Recycled | 10.084 | 8.036 | 10.83 | 11.954 | 12.198 | 12.836 | 14.346 | 12.696 | 10.908 | 10.63 | 8.83 | 9.29 | 132.638
WATER AUDIT TOTALS
excludes recycled water accounts
| Billed Metered Authorized Consumption: |  |  | 1051.3309 | MG | includes SF Residential, MF Residential, Commerical/Institutional, Industrial, Landscape Irrigation (potable), and Municpal uses
| Billed Unmetered Authorized Consumption: |  |  | N/A |  | all billed customers have a meter
| Unbilled Metered Authorized Consumption: |  |  | 17.2704 | MG | this includes our own facility use; all metered and read monthly but not revenue generating
| Unbilled Unmetered Authorized Consumption: |  |  |  |  | this includes minimal flushing, fire-fighting, and fire-flow testing - we currently do not track so default applied
Reminders for Billed Metered Authorized Consumption (BMAC) Supporting Documentation:
* volume billed per customer class (or rate code, or account type) by month
* highlight and exclude any non-potable customer classes
* highlight any customer classes (like water utility or facility use) that does not generate revenue (unbilled!)